Fixed-Speed-Pump Optimal Water Flow (OWF)

Model, Algorithms, and Implementation Logic of the Python C-OWPF Water Engine

CVXPY + HiGHS + EPANET (epyt) implementation

Companion methodology note to the MATLAB C-OWPF code of “Successive Linear Approximations for Optimal Decision Making in Interdependent Electric and Water Distribution Networks” (IEEE Access, Access-2024-18604)

# Contents

# 1. Scope

This note documents the water-side Optimal Water Flow (OWF) problem for fixed-speed pumps (FSPs) as implemented in the Python package owf. It is a faithful translation and extension of the MATLAB C-OWPF water engine: the modeling language is CVXPY, the mixed-integer solver is HiGHS (with SCIP as a numerical fallback), and all EPANET input parsing, hydraulic ground truth and validation use the EPANET-Python-Toolkit (epyt). Variable-speed pumps, pressure-reducing valves and the power-distribution coupling of the full C-OWPF remain future phases; everything here concerns the FSP water problem.

The engine schedules pump on/off states and network hydraulics over a horizon of T hourly steps to minimize pumping energy cost under a (possibly time-varying) electricity price, subject to linearized hydraulic physics, tank dynamics and head bounds. Every result is checked against EPANET by re-simulating the optimized schedule in the true nonlinear hydraulics.

# 2. Network representation and notation

A water distribution network is a graph of N nodes (junctions, tanks, reservoirs) and L links (pipes, pumps, and optionally switched bypass pipes). All structure is encoded in constant topology matrices built once from the EPANET file:

| Symbol | Size | Meaning |
| --- | --- | --- |
| Π (Pi) | N × L | node–arc incidence: +1 at a link's from-node, −1 at its to-node |
| Π̃ (Pi_telda) | P × N | rows of Πᵀ for pipes only (energy equation) |
| Π′ (Pi_prime) | P × L | selects pipe flows out of the full flow vector |
| Π_J (Pi_reduced) | J × L | incidence rows for junctions only (mass balance) |
| Λ (Lambda) | M × L | selects pump flows |
| Θ (Theta) | R × N | selects reservoir nodes |
| Τ (Tau) | N × K | selects tank nodes (columns) |
| Κ (Kappa) | J × N | selects junction nodes |
| Ω (Omega) | P × P | diagonal Hazen–Williams pipe resistances ω |
| Δ (Delta) | K × K | diagonal tank cross-section areas |
| Π̃_b, Π′_b, Ω_b, S | — | bypass analogues: incidence, selector, resistance, and bypass→pump map |

The Hazen–Williams resistance of pipe p with roughness C, diameter D (inches) and length Lₚ (ft), for flow in GPM, is

ωp = 10.4622 C−1.852 D−4.871 Lp

Pipes whose EPANET initial status is Closed are excluded from the energy equation and pinned to zero flow. Pipes designated as switched bypasses are removed from the ordinary pipe set and treated in Section 5.

# 3. Decision variables

- Flows  q ∈ ℝ^{L×T} — volumetric flow on every link at every hour (GPM)

- Heads  h ∈ ℝ^{N×T} — hydraulic head at every node (ft)

- Ppump  P ∈ ℝ^{M×T} — electrical power of each pump (kW after the cₘ scaling)

- OnOff  z ∈ {0,1}^{M×T} — pump on/off status (the only integer variables)

- Hdummy, TankFlow_aux — tank level state and net tank inflow auxiliaries

With the linearization coefficients frozen (Section 6), every constraint below is linear; the per-iteration problem is therefore a MILP, and a pure LP whenever the schedule z is fixed.

# 4. The per-iteration optimization problem

## 4.1 Objective — pumping energy cost

min  tπt mPm,t1000

where πₜ is the electricity price (time-of-use pattern or flat). The reported comparison cost always re-evaluates the true nonlinear power at the solved flows (Section 8), never the linearized surrogate.

## 4.2 Mass balance at junctions

ΠJ qt = −dt

with dₜ the junction demand vector taken directly from EPANET's computed time series, so pattern wrapping, default patterns and mixed pattern lengths agree with EPANET exactly.

## 4.3 Pipe head loss (Hazen–Williams) and its monomial linearization

The exact pipe equation is nonconvex:

Δhp = ωp |q|0.852 q

Following the monomial linearization of the paper, the coefficient is frozen at the previous iterate q̄ and the constraint enforced as

Π̃ ht = Cp,t + Π′ qt ,   Cp,t = q̄ (ω |q̄|0.852 − 1)

so that at q = q̄ the linearized equation reproduces the exact head loss. This is the relation the successive-linearization loop refreshes each iteration.

## 4.4 Pump hydraulics with a general exponent ν

The pump head–gain curve is not restricted to a quadratic. For pump m,

Δhm = −( h0,m − σm fν )

with shutoff head h₀, curve coefficient σ and exponent ν. The monomial linearization freezes σ f^{ν−1} at the previous pump flow f̄:

C1M = −h0 ,   C2M = σ f̄ν−1 ,   C1M + C2M·f ≤ 0

EPANET single-design-point curves are exactly quadratic by construction (ν = 2, Section 6); multi-point curves receive their fitted exponent (Net3: ν = 1.77 and 1.09).

## 4.5 FSP electrical power and its first-order Taylor model

The true FSP power and its derivative for general ν are

P(f) = cm ( h0 − σ fν ) f

P′(f) = cm ( h0 − (ν+1) σ fν )

which reduces to the familiar cₘ(h₀ − 3σf²) when ν = 2. The Taylor model about f̄ gives the linear constraint

P = A′ f + B′ z ,   A′ = P′(f̄) ,   B′ = P(f̄) − P′(f̄) f̄

The power conversion constant is cₘ = 0.7457 / (3960 · 0.81) (GPM·ft → kW at 81% efficiency).

## 4.6 Pump on/off gating (Big-M) and flow bounds

M (z − 1) ≤ ΛΠᵀ h − ( C1M + C2M f ) ≤ M (1 − z)

0 ≤ f ≤ fmax z ,   fmax = ( h₀ / σ )1/ν

When z = 1 the pump-curve equality is enforced and flow may be positive; when z = 0 the curve is relaxed and the flow is forced to zero. The Big-M constant is scaled per network (Section 9.1).

## 4.7 Tank dynamics, bounds and terminal condition

Each tank integrates its net inflow u (selected by Τᵀ(−Π)q) through a running-sum (lower-triangular) matrix B:

Hi,t = Hi,0 + δAiτ≤tui,τ

with δ = 8.0208 converting GPM-hours to cubic feet and Aᵢ the tank area. The tank node head equals the previous step's level; levels stay within [Hᵢᵐⁱⁿ, Hᵢᵐᵃˣ]; and the terminal level must not fall below the mean of the initial and minimum heads:

Hi,T ≥ ½ ( Hi,0 + Hi min )

## 4.8 Reservoir and junction head constraints

Θ h = Θ helev ,    Κ hmin ≤ Κ h ≤ Κ hmax

Reservoir heads are pinned to their elevations; junction heads are bounded below by elevation (non-negative pressure) and above by a loose cap.

# 5. Special link logic: closed pipes, switched bypasses, availability

## 5.1 Permanently closed pipes

A pipe whose EPANET initial status is Closed carries no flow and no Hazen–Williams relation. Modeling it as an ordinary pipe creates a phantom connection whose forced head-loss equation corrupts the whole solution (on Net3 this alone produced a 96.7 ft residual). Such pipes are excluded from Π̃/Ω and constrained to q = 0.

## 5.2 Switched bypass (parallel pipe coupled to a pump)

Net3 contains the pattern: a bypass pipe in parallel with a pump, open exactly when the pump is off (EPANET rules: Link 330 CLOSED IF pump 335 is running, OPEN otherwise), letting the elevated tank feed the network by gravity. With z the controlling pump's status, q_b the bypass flow and C_b its monomial head-loss coefficient (same construction as Cₚ):

−M (1 − z) ≤ qb ≤ M (1 − z)

−M z ≤ Π̃_b h − ( Cb + qb ) ≤ M z

Pump on (z = 1): the bypass is closed — zero flow, head relation relaxed. Pump off (z = 0): the bypass behaves as a normal pipe. The same status logic is imposed when replaying any schedule in EPANET; forgetting this made the replay meaningless (heads diverged by 10⁸ ft) because deleting EPANET's rules left the bypass stuck closed.

## 5.3 Pump availability windows

A pump drawing from a time-limited source (Net3's lake pump: available hours 1–14 only) is forced off outside its window: zₘ,ₜ = 0 for t outside [start, end). Candidate schedules in the optimizer are masked by the same rule.

# 6. Pump curves derived from EPANET (general ν)

Coefficients are derived from each network's EPANET head curve rather than hard-coded per network — hard-coded tables drifted from the actual .inp files in the original MATLAB (the 3-node case carried small-pump values while its file defined the large pump, making demand physically unmeetable).

- Single design point (Q_d, H_d): EPANET's convention forces an exact quadratic through (0, 1.3333·H_d), (Q_d, H_d), (2Q_d, 0):

h0 = 1.3333 Hd ,   σ = h0(2Qd)2 ,   ν = 2

- Multi-point curve: take h₀ as the shutoff head, then fit ν and σ by the log-linear regression

log( h0 − Hj ) = log σ + ν log Qj

- No head curve (e.g. EPANET constant-power pumps, as in KY3): the FSP head-gain form cannot represent the pump; setup raises a clear error naming the pumps and asks for explicit [h₀, σ, ν] instead of silently producing NaN results.

# 7. Successive linearization algorithm

With coefficients frozen, one MILP is solved; the solution provides a new linearization point; repeat until the stacked iterate stops moving:

εk = [ h ; q ; z ] ,    ‖εk − εk−1‖₂ < 0.5

- Initialization: an EPANET extended-period simulation supplies the initial flows/heads (choice = 1), matching the MATLAB Initial_Values path; tank rows are reset to their initial heads.

- Damping (trust region): on hard networks the relinearization point may be blended with the previous one, q̄ₖ₊₁ = γ qₖ + (1−γ) q̄ₖ, γ ∈ (0,1] — the Python analogue of the damping line left commented in the MATLAB.

- Best-iterate fallback: the loop snapshots the best solution so far (ranked by bound violation, then step size). A late ill-conditioned solve can stop the loop but can no longer destroy the run.

- Mass-balance warm-up (MATLAB parity flag): the original code disabled mass balance for the first 10 iterations; Python enforces it from iteration 0 by default and keeps the historical behavior behind a flag.

On tree networks (8-node, 3-node) this plain loop converges in 2–4 iterations. On looped networks it does not — which motivates Section 8.

# 8. Warm starts, fixed schedules, and schedule optimization

## 8.1 Why looped networks fail from the default start

In a looped network the tank head is determined twice — by the hydraulic path from the reservoir and by the tank integrator — and a linearization built at one operating point cannot reconcile the two far from that point. The iteration either goes infeasible immediately (Net1, Net2) or drifts to a nonsensical fixed point (pump on 24 h, tank overfilling). Diagnosis method: evaluate every constraint's residual at EPANET's own solution; the constraint whose residual is large at a known-physical point is the modeling gap.

## 8.2 Soft head bounds (penalty convex–concave)

For the search phases, tank/junction head bounds and the tank terminal condition are relaxed with nonnegative slacks s penalized in the objective with a growing weight ρₖ (capped). Every MILP stays feasible; a solution counts as converged only if max s ≤ feas_tol.

## 8.3 EPANET multi-start

Candidate on/off schedules — EPANET's own rule-based schedule, all-on, all-off, cheapest-half-hours — are each imposed in an EPANET simulation, and the resulting physically consistent flows seed the linearization. The best (least-violating, then cheapest) start wins.

## 8.4 Fixing the schedule: MILP → LP

Once a good binary schedule is chosen it is substituted as a constant. Every occurrence of z becomes arithmetic: flow bounds collapse to f = 0 on off-hours, the Big-M pump curve becomes an equality on on-hours, the power model loses its binary term. The per-iteration problem is then a pure LP whose fixed-point iteration is smooth — the discrete schedule-flipping that prevents convergence is gone, and because the seed comes from EPANET under that very schedule, convergence typically takes one iteration. solve_from_epanet packages exactly this: reproduce EPANET's operation as a validated baseline (the only reliable mode for Net3's 50-binary problem).

## 8.5 Honest schedule optimization

Key finding: a single MILP at a frozen linearization cannot judge a schedule far from its linearization point — the coefficients simply do not apply there — so it always returns the incumbent. This failure is silent; it was exposed only by testing on Net2, where a far cheaper schedule was independently known. Consequently optimize_schedule never lets the linearization predict; every candidate is evaluated honestly:

- fix the candidate schedule → converge the LP → score by the true nonlinear cost

C(q) = tπtmcm( h₀ − σ fν ) f1000

- candidate family: price-quantile schedules (run only during the cheapest 25/40/50/60/75/90% of hours), all-on, plus one MILP proposal at the incumbent's linearization

- 1-opt polish: flip single pump-hours (most expensive hours first); accept a flip only if it stays feasible and lowers the true cost — the result is locally optimal w.r.t. single-hour changes

- ranking: feasible (slack ≤ tolerance) first, then lowest true cost; availability windows are enforced on every candidate

# 9. Numerical robustness

## 9.1 Adaptive Big-M

A fixed M = 10⁷ ill-conditions HiGHS when heads are O(10²) ft and pipe resistances are O(10⁻⁵) (Net3 returned status UNKNOWN). M is scaled per network from the head span and the actual EPANET operating flows (not the pump's theoretical shutoff flow, which can be an order of magnitude larger):

M = max( 10⁴ ,  20 · span(h) ,  5 · max|q EPANET| )

## 9.2 Solver fallback and failure containment

- solver chain HiGHS → SCIP: an iterate HiGHS reports UNKNOWN is retried on SCIP before giving up; this converted several garbage candidate scores (∞, 10⁴-ft slacks) into valid evaluations

- a single failed solve stops the loop gracefully and returns the best snapshot instead of crashing

## 9.3 CVXPY parameterization discipline

- linearization coefficients (Cₚ, C1M, C2M, A′, B′, C_b) are cp.Parameters — the problem compiles once and only numbers change between iterations

- a fixed schedule enters as a plain constant array, not a Parameter — Parameter×Parameter products are not DPP and would force a full recompilation every iteration

## 9.4 EPANET interfacing

- epyt keeps one global toolkit instance, so every simulation opens a fresh handle from the .inp path; reusing a long-lived handle after other loads produced stale-handle crashes

- replaying a schedule deletes EPANET's controls/rules and drives pump AND bypass statuses hour-by-hour; demand profiles are read from EPANET's computed series

# 10. Validation methodology

Two comparisons, in increasing strictness:

- Rule-based comparison (validate): error norms against EPANET running its own controls — a sanity check only, since the optimizer legitimately chooses a different operating point.

- Schedule-imposed replay (validate_schedule, the paper's Fig. 4 check): impose the optimized on/off schedule (and bypass logic) in EPANET, re-simulate the true nonlinear hydraulics, and compare heads and flows hour by hour. Metrics: max |Δhead| (ft), max |Δflow| (GPM), minimum junction pressure (> 0 ⇔ hydraulically feasible), tank levels within bounds.

Accuracy achieved (replay of each network's solved schedule):

| Network | max ¦Δhead¦ (ft) | max ¦Δpump flow¦ (GPM) | Note |
| --- | --- | --- | --- |
| 8-node | 0.15 | 1.0 | direct mode |
| 3-node | 0.005 | 0.01 | direct mode |
| Net1 | 0.005 | 0.002 | warm-start |
| Net2 | 0.013 | 0.001 | warm-start |
| Net3 | ≈4.5 | ≈66 | EPANET itself carries small negative pressures here |

Convergence is not the limiter on Net3. A controlled experiment tightened the fixed-schedule LP from (tol 0.5, 20 iterations) to (tol 0.05, 150 iterations): the iterate-change norm fell only from 1.89 to 1.21 — a per-variable movement of fractions of a GPM — while every EPANET-replay metric remained identical to 0.01 GPM (max |Δhead| 4.545 ft; loop-pipe gaps 547/512/512 GPM). The linearized model has reached its fixed point; the residual ≈5% mid-day re-split among parallel loop pipes (hours 6–14, all pumps off) is structural: EPANET's discrete tank-level events re-split the gravity supply abruptly (the smooth tank integrator has no such switch), pump-transition hours are sampled at hour boundaries while EPANET sub-steps within the hour, and EPANET itself operates with slightly negative pressures there (the constant 1.9 ft slack in every iterate). Pumps, trunk flows, tank trajectories and cost are unaffected. Modeling EPANET-style tank closure (one additional binary per tank-hour) is the remaining lever and is planned together with the PRV phase.

# 11. Networks and results

| Network | Size (nodes/links) | Features | Recommended mode | Optimize: saving vs EPANET |
| --- | --- | --- | --- | --- |
| 8-node | 8 / 9 | tree, 1 pump, 1 tank | direct | 29.9% |
| 3-node | 3 / 2 | tree, 1 pump, 1 tank | direct | 70.7% |
| Net1 | 11 / 13 | looped, 1 pump, 1 tank | warmstart | 45.4% |
| Net2 | 36 / 40 | looped, 1 pump, 1 tank | warmstart | 77–81% |
| Net3 | 97 / 119 | looped, 2 pumps (ν≠2), 3 tanks, 2 reservoirs, switched bypass, availability window | epanet | 0% (honest) |
| KY3 | 275 / 371 | 5 constant-power pumps (no head curves) | archived | — |

Every reported saving is confirmed by the EPANET replay: positive junction pressures and in-bounds tanks. Net3's 0% is a validated negative result: its built-in tank-level controls are already near-optimal — pump 335 runs exactly the five cheapest hours, the lake pump uses all of its 14 permitted hours, and every price-quantile alternative either costs more or violates a tank bound by 12–21 ft. Improving on it would require candidates aware of the per-tank refill structure.

# 12. Implementation map

| MATLAB (C-OWPF) | Python module | Role |
| --- | --- | --- |
| Main_OWF_IEEE_ACCESS.m | main_owf.py | interactive/CLI driver, case runner, comparison tables |
| WDN_setup_* / definebounds | owf/network.py | assemble WDN, bounds, prices, adaptive Big-M |
| Prepare_net / read_inp / init_epanet | owf/epanet_io.py | parse .inp, pump-curve derivation, simulations, schedule replay |
| ConnectionMatrices_WDN.m | owf/connection_matrices.py | topology matrices incl. bypass set |
| Initial_Values_WDN.m | owf/initial_values.py | initial linearization point |
| CalculateNewIterationValues.m | owf/linearization.py | Cₚ, C1M, C2M, A′, B′, C_b refresh |
| define*_CVX.m (one file each) | owf/constraints.py | every constraint as one function; soft variants |
| WDN_OWF_IEEEACCESS_cvx.m | owf/solver.py | successive-linearization loop, fallbacks |
| — (new) | owf/warmstart.py | multi-start, solve_from_epanet, optimize_schedule |
| — (new) | owf/validation.py, owf/plots.py | EPANET replay checks; diagnostic plots |